# Main elements library of the user interface
Name:	wlb_Main
Founded:	september 2007
Version:	0.5.0
State:	Open (GPL)
Author:	Roman Savochenko, Maxim Lysenko
Description:	Provides the library of the main elements of the user interface.
Address:	DB is in the file: SQLite.vcaBase.wlb_Main (LibsDB.vcaBase.db)

## About the library
The library is created to provide mnemonic elements of the user interface. The library is built on the basis primitives of widgets and JavaLikeCalc module, allowing to create calculations on the Java-like language.
It is possible to connect the library of mnemonic elements of user interface to the project of the OpenSCADA station by downloading the attached file of the database, placing it in in the database directory of the station's project and creating the database object for the DB module "SQLite", indicating the database file in the configuration.
The library contains about two dozen graphic elements, often sought when forming the user interface of process control. Names and text options are available in three languages: English, Russian and Ukrainian.
## 1. Analog show (anShow)
The element, shown in Fig. 1, is used to display the current value of the analog parameter and modes of regulator, if the parameter is regulator. Also, this element generates alarms on the relevant parameter settings.

Fig.1. "Analog show" widget in the development and runtime modes (left to right).
### Using - Development
This widget can be used by developer to create mimics to display the values of analog parameters and PID regulators. To use it you need to add this widget to mimic and link to the data source parameter.
### Using - Runtime
At runtime mode, you can obtain the passport for parameter by clicking the right mouse button on the body of the widget. The passport will present all the properties of the parameter. Pressing the left mouse button in the body of the widget the control panel will appear parameter, and the selection of this widget will be displayed with blinking frame.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
pErr	Error	String	Input link	Parametr|err	Code and text of the error of the parameter. It is used to generate alarm. The following error codes are processed: / 1,2 - failure, parameter is not valid; / 3 - above the admissible limit; / 4 - below the admissible limit; / 5 - above normal; / 4 - below normal.
pModeA	Regulator mode (auto)	Boolean	Input link	Parametr|auto	When adjusted on the left of the value the large letter "A" is displayed.
pModeC	Regulator mode (cascade)	Boolean	Input link	Parametr|casc	When adjusted on the left of the value the large letter "C" is displayed.
pName	Parameter's name	String	Input link	Parametr|NAME	Short name of the parameter displayed over the value.
pPrec	Precision	Integer	Input link	Parametr|prec	Number of decimal places for value.
pVal	Parameter's value	Real	Input link	Parametr|var	Direct parameter's value.
redEVAL	Red parameter name in case of failure	Boolean	Constant		By default, the color of the parameter's name for the "failure" state(EVAL value) is gray. But some critical for the process parameters must have the "failure" state displayed with the red parameter's name.
spName	Speech name	String	Constant		The name of the parameter for speech synthesis during the formation of alarm messages taking into account accents of words, pauses, etc.

## 2. Analog show 1 (anShow1)
The element, shown in Fig. 2, is used to display the current value of the analog parameter with a one-character prefix of the type of measured value.

Fig.2. "Analog show 1" widget in the development and runtime modes (left to right).
### Using - Development
This widget can be used by developer to create mimics to display the values of analog parameters. o use it you need to add this widget to mimic and link to the data source parameter.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
pName	Parameter's name	String	Constant	Parametr|NAME	One-character prefix of the type of measured value.
pVal	Parameter's value	Real	Input link	Parametr|var	Direct parameter's value.
pPrec	Precision	Integer	Input link	Parametr|prec	Number of decimal places for value.

## 3. Element cadr (ElCadr)
The element, shown in Fig. 3, is essentially a universal control panel of various devices:
- analogue: indications, manual input values and regulators (analog and pulse);
- discrete: valves, automatic shut off valves, motors, fans and switches.

Fig.3. "Element cadr" widget in the development mode.
### Using - Development
This widget is not intended for special placement and configuration of the user, as laid down in the "Signal groups" template and if the new project is created from this template, the call of the widget is done automatically, with its display in the control panel area when you select a widget of the parameter, which provides the parameter's control, for example, previously considered "anShow ".
### Using - Runtime
Fig. 4 shows various examples of this element in the runtime mode.

Fig.4. "Element cadr" widget in the runtime mode.
Modes:
- Indications of the analog parameter. In this mode, there is no any control, and there are only units displaying, the value's histogram and the name of the parameter.
- Manual input of an analog parameter. In addition to displaying indications of analog parameters the buttons to enter a new value are displayed. Enter of the value is displayed in the field at the top, in the white rectangle. To validate the input, press the left mouse button in the area of white rectangle. Without validation the typed value will be reset after a few seconds.
- PID regulator's mode. To the value of a variable and its histogram are added values and histograms of set point and out of the PID regulator, the buttons to enter a new value of the set point or out, as well as the mode adjustment button and the field to display the current mode. Also, for the user with appropriate privileges it is available the button to go to the frame to set the coefficients of PID regulator. In the case of pulsed PID instead of histogram of the analog output it is displayed the status of pulse output with the help of triangles "Up" and "Down" and the manual entry of output leads to direct formation of pulse, respectively down or up.
- Mode of a discrete device. In this mode the name of the parameter and the field of discrete building of the parameter are displayed. The field of discrete building contains the current state of discrete device on the left and the buttons of commands on the right. There are two states of the device: "Open", "Closed" and the three commands: "Open", "Close", "Stop". The names of states and commands can be adjusted during set up. Changing the state of the logic device is determined by pressing the corresponding command.
For any displayed or controlled parameter the passport can be obtained in runtime mode by clicking the right mouse button on the contour field. The passport will present to all the properties of the parameter.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
prmId	Parameter:identifier	String	Input link	Parametr|SHIFR	Parameter's identifier is used to place the record the operator's actions to the report.
prmShifr	Parameter:code	String	Input link	Parametr|NAME	Short name of the parameter, code. It is placed below the frame.
prmDescr	Parameter:description	String	Input link	Parametr|DESCR	Description of the parameter is used to place the record the operator's actions to the report.
prmColor	Parameter:border color	String	Input link	Parametr|color	Sets the border color of the contour.
Parameters of Analog Device
prmDemention	Parameter:dimension variable	String	Input link	Parametr|ed
prmPrec	Precision	Integer	Input link	Parametr|prec	Number of decimal places in parameter, step change for the manual input of values, as well as set point and out of the PID regulator.
prmVar	Parameter:variable	Real	Full link	Parametr|var	Directly to the analog value of the parameter.
max	Parameter:maximum	Real	Input link	Parametr|max	Upper limit value of the parameter.
min	Parameter:minimum	Real	Input link	Parametr|min	Minimum limit values of the parameter.
prmAMax	Upper alarm border	Real	Input link	Parametr|aMax
prmAMin	Lower alarm border	Real	Input link	Parametr|aMin
prmWMax	Upper warning border	Real	Input link	Parametr|wMax
prmWMin	Lower warning border	Real	Input link	Parametr|wMin
Manual Analog Input
prmVarIn	Parameter:variable input	Real	Full link	Parametr|varIn	Output for manual input of an analog value of the parameter. The presence of this parameter is an indication that the parameter - is determined as "Manual analog input.
PID regulator
prmAnalog	Parameter:analog regulator	Boolean	Input link	Parametr|analog	Sign of the analog regulator, in case of the absence of this parameter the regulator is an analog one.
prmAuto	Parameter:automate	Boolean	Full link	Parametr|auto	Mode of the regulator, "Automatic".
prmCasc	Parameter:Cascade	Boolean	Full link	Parametr|casc	Mode of the regulator, "Cascade".
prmSp	Parameter:set point	Real	Full link	Parametr|sp	PID regulator's set point, it can be set by the user.
prmImpQdwnTm	Parameter:imp. out down	Boolean	Input link	Parametr|impQdwn	Output "Down" for impulse regulator.
prmImpQupTm	Parameter:imp. out up	Boolean	Input link	Parametr|impQup	Output "Up" for impulse regulator.
prmOut	Parameter:output	Real	Full link	Parametr|out	Analog PID regulator output for display and manual input of the output value of PID in manual mode.
prmManIn	Parameter:manual input	Real	Full link	Parametr|manIn	Manual input of the new output value of PID regulator in manual mode.
Parameters of discrete devices
prmCom	Parameter: Command - "Open"	Boolean	Full link	Parametr|com
prmClose	Parameter: Command - "Close"	Boolean	Full link	Parametr|close
prmStop	Parameter: Command - "Stop"	Boolean	Full link	Parametr|stop
prmOpenSt	Parameter: State - "Opened"	Boolean	Input link	Parametr|st_open
prmCloseSt	Parameter: State - "Closed"	Boolean	Input link	Parametr|st_close
digComs	Parameter:digital commands	String	Input link	Parametr|digComs	Names and colors of buttons of commands in the format: {On}[-color]:{Off}[-color][:{Stop}[-color]]. Default colors are: green, red and yellow.
digStts	Parameter:digital states	String	Input link	Parametr|digStts	Names and colors of labels of states in the format: {On}[-color]:{Off}[-color]. Default colors are: green and red.

## 4. Contours group (grpCadr)
Element, shown in Fig. 5, provides for simultaneous monitoring and control of several contours up to eight, includes both instances of the widget "Element cadr for each contour, and a widget "Diagram" to monitor the trends of the contours and viewing history .
Fig.5. "Contours group" widget in the development mode.
### Using - Development
This widget is designed to perform the role of page-template, and should therefore be placed directly in the project's tree. The project-template "signal groups" for each signal object that widget-frame is included in the role of a template that allows you to create on its basis a set of pages of groups of contours. For each widget-frame, it can be connected up to eight parameters by setting the links. Contours for which there is no set links will be hidden at runtime.
### Using - Runtime
In runtime mode, the contours and trends, for which links have been set, are displayed. Control of the parameters by contours, respectively described in detail in the section of the "Element cadr (ElCadr)" widget. In addition to this you can control the trends display properties, which requires the left mouse button to click in the trend's area and by means of appeared trend's control panel to make the necessary actions.
Fig. 6 is an example of this element in the runtime mode.
Fig.6. "Contours group" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
grpName	Group name	String	Constant		Group's name
Element {n} from 1 to 8.
el{n}	The list of linking parameters corresponds to the list of the "Element cadr (ElCadr)" widget

## 5. Views page's element (ElViewCadr)
Element, shown in Fig. 7, serves as the basis for overview frames panel and is not usually used independently. Element reflects the text information about a parameter in the form of the name and value, and a graph (trend) of the parameter for a small (adjustable) period of time to observe the current trend of the parameter with auto-scaling on the value's scale.

Fig.7. "Views page's element" widget in the development mode.
### Using - Development
Though this widget is not intended for independent use, in isolation from frames panel, it can be used, for example, by placing it to the mimic and linking with the data source parameter.
### Using - Runtime
At runtime mode, you can obtain the passport for parameter by clicking the right mouse button on the body of the widget. The passport will present all the properties of the parameter. Pressing the left mouse button in the body of the widget the control panel will appear parameter, and the selection of this widget will be displayed with blinking frame.
Fig. 8 shows various examples of this element in the runtime mode.

Fig.8. "Views page's element" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
name	Name	String	Input link	Parametr|NAME	Parameter name, code, for display in the name's field.
addr	Address	Address	Input link	Parametr|var	Address to the attribute of the parameter's values for trend's building.
var	Variable	Real	Input link	Parametr|var	Direct value of the parameter to display in value's field.

## 6. Overview frames panel (ViewCadr)
Element, shown in Fig. 9, serves to show the current trends for the parameters of the signal object up to 24 pieces, supports scaling elements depending on their number. Consists of widgets "views page's element (ElViewCadr)".
Fig.9. "Overview frames panel" widget in the development mode.
### Using - Development
This widget is designed to perform the role of template-page, and should therefore be placed directly in the project's tree. The project-template "signal groups" for each signal object that widget-frame is included in the role of a template that allows you to create on its basis a set of pages of groups of overview frames panel. To each widget-frame can be connected to the 24-parameter by setting the links. Trends for which there is no set links will be hidden at runtime, and when it is necessary the expansion and scaling of linked ones will be done to fill the area of the widget.
### Using - Runtime
In the runtime mode the trends' contours are displayed, for which links have been set. Control of the parameters from contours, respectively described in details in the section "views page's element (ElViewCadr)" widget.
Fig. 10 shows an example of this element in the runtime mode.
Fig.10. "Overview frames panel" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
name	Name	String	Constant		Frame's name
Element {r}_{c}, where {r} - rows from 1 to 4 and {c} - columns from 1 to 6.
el{r}_{c}	The list of linked parameters corresponds to the list of ones of the "Views page's element (ElViewCadr)" widget

## 7. Graphics group element (ElViewGraph)
Element, shown in Fig. 11, is provided to create graphics groups. Element contains information about a parameter, the regulator's mode if the parameter is such, the units of analog parameter, as well as the color corresponding to the parameter's trend.

Fig.11. "Graphics group element" widget in the development mode.
### Using - Development
Though this widget is not intended for independent use, in isolation from graphics groups, it can be used, for example, by placing it to the mimic and linking with the data source parameter.
### Using - Runtime
At runtime mode, you can obtain the passport for parameter by clicking the right mouse button on the body of the widget. The passport will present all the properties of the parameter. Pressing the left mouse button in the body of the widget the control panel will appear parameter, and the selection of this widget will be displayed with blinking frame.
Fig. 12 shows various examples of this element in the runtime mode.

Fig.12. "Graphics group element" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
name	Name	String	Input link	Parametr|NAME	Parameter name, code, for display in the name's field.
addr	Address	Address	Input link	Parametr|var	Address to the attribute of the parameter's values for trend's building.
color	Trends color	String	Constant
Parameters of Analog Device
ed	Dimension	String	Input link	Parametr|ed
prec	Precision	Integer	Input link	Parametr|prec	Number of decimal places in parameter.
max	Maximum	Real	Input link	Parametr|max	Upper limit value of the parameter.
min	Minimum	Real	Input link	Parametr|min	Minimum limit values of the parameter.
aMax	Upper alarm border	Real	Input link	Parametr|aMax
aMin	Lower alarm border	Real	Input link	Parametr|aMin
wMax	Upper warning border	Real	Input link	Parametr|wMax
wMin	Lower warning border	Real	Input link	Parametr|wMin
pModeA	"Automate" regulator's mode	Boolean	Input link	Parametr|auto	Mode of the regulator, "Automatic".
pModeC	"Cascade" regulator's mode	Boolean	Input link	Parametr|casc	Mode of the regulator, "Cascade".
Parameters of discrete devices
digComs	Digital commands	String	Input link	Parametr|digComs	Names and colors of buttons of commands in the format: {On}[-color]:{Off}[-color][:{Stop}[-color]]. Default colors are: green, red and yellow.
digStts	Digital states	String	Input link	Parametr|digStts	Names and colors of labels of states in the format: {On}[-color]:{Off}[-color]. Default colors are: green and red.
digRevers	Revers	Boolean	Constant		Discrete signal reverse.

## 8. Graphics group (grpGraph)
Element, shown in Fig. 13, is provided for simultaneous observation of a trend and control the parameters of the signal object, includes both instances of the widget "Graphics group element (ElViewGraph) " for each parameter and widget "Diagram" to monitor the parameters' trends and browsing history.
Fig.13. "Graphics group" widget in the development mode.
### Using - Development
This widget is designed to perform the role of page-template, and should therefore be placed directly in the project's tree. The project-template "signal groups" for each signal object that widget-frame is included in the role of a template that allows you to create on its basis a set of pages of graphics group. For each widget-frame, it can be connected up to eight parameters by setting the links. Trends for which there is no set links will be hidden at runtime.
### Using - Runtime
In runtime mode, the trends, for which links have been set, are displayed. Control of the parameters from the text elements of the trends, respectively described in detail in the section of the "Graphics group element (ElViewGraph)" widget. In addition to this you can control the trends display properties, which requires the left mouse button to click in the trend's area and by means of appeared trend's control panel to make the necessary actions.
Fig. 14 shows an example of this element in the runtime mode.
Fig.14. "Graphics group" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
grpName	Group name	String	Constant		Group name
Element {n} from 1 to 8.
el{n}	The list of linking parameters corresponds to the list of the "Graphics group element (ElViewGraph)" widget

## 9. Result graphic's element (ResultGraphEl)
Element, shown in Fig. 15, is provided to create result graphics. Element allows you to display trends on the five parameters for a specified period of time till the current time.

Fig.15. "Result graphic's element" widget in the development mode.
### Using - Development
Though this widget is not intended for independent use, in isolation from result graphics, it can be used, for example, by placing it to the mimic and linking with the data source parameter.
Fig. 16 shows an example of this element in the runtime mode.

Fig.16. "Result graphic's element" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
title	Title	String	Constant		It is displayed above the graph. If the title is missing the trend's field will expand up.
Trend {n} from 1 to 5.
p{n}_addr	Parameter{n}:address	Address	Input link	Parametr_{n}|var	Address to the value's attribute for {n} trend's building.
p{n}_clr	Parameter{n}:color	Color	Constant	Parametr_{n}
p{n}_max	Parameter{n}:maximum	Real	Input link	Parametr_{n}|max	Upper limit of the trend.
p{n}_min	Parameter{n}:minimum	Real	Input link	Parametr_{n}|min	Lower limit of the trend.
p{n}_name	Parameter{n}:name	String	Input link	Parametr_{n}|NAME	The short name of the parameter to display in the field on the left.

## 10. Result graphics (ResultGraph)
Element, shown in Fig. 17, is used to display the trends of the parameters of the whole visualization project.
Fig.17. "Result graphics" widget in the development mode.
### Using - Development
This widget is designed to perform the role of page-template, and should therefore be placed directly in the project's tree. In the project-template "signal groups" on the root page level there is special virtual page "Result graphics" with the result graphics template, that allows you to create on its basis a set of pages of result graphics. To each widget-frame can be connected to the 16*5 parameters by setting the links. Trends, for which there is no set links, will be hidden at runtime, and when it is necessary the expansion and scaling of linked ones will be done to fill the area of the widget.
### Using - Runtime
In runtime the contours of the trends, for which the links are set, are displayed.
Fig. 18 shows an example of this element in the runtime mode.
Fig.18. "Result graphics" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
grpName	Group name	String	Constant		Group name
Element {n} from 1 to 16.
el{n}	The list of linking parameters corresponds to the list of the "Result graphic's element (ResultGraphEl)" widget.

## 11. Regulator's control panel (cntrRegul)
Element, shown in Fig. 19, is used for adjustment of PID regulator, includes information about the parameter-regulator, fields of the regulator's settings, and the "Diagram" widget to monitor the trends of the regulator and browsing history.
Fig.19. "Regulator's control panel" widget in the development mode.
### Using - Development
This widget can be used as a panel, called from the control of panel of the parameters "ElCadr", as well as a template-page. Widget should be placed directly in the project's tree, namely to the panels' container, where the dynamic linking will be implemented to the regulator's parameter. To create the static list of the regulator's settings contours, with the possibility of paging in it, you must place them in a container of regulator's contours "greg" of each signal object and statically link them with the corresponding parameter, and to ensure equality of the panel's ID and linked parameter.
### Using - Runtime
In the runtime mode the following fields are displayed:
- name of the regulator's parameter;
- field with the properties of regulator consisting of: identifier, name, description, units, set point, variable output, scale and mode;
- coefficients of regulator's settings: Kp, Ki, Ti, Kd, Td, Tzd, Zi, H1, H2, K1, K2, K3, K4, Tpl, Tml и Rfkt.
- area of the diagram with displaying trends: variable (green), set point (blue), the analog output (cyan), regulator's mode "Automatic" (magenta) and digital outputs.
Users have the ability to change the PID regulator's coefficients: mode, set point, out and immediately to see the reaction on the diagram. In addition, the user can learn the history of the regulator, which requires the left mouse button click in the graph area and by means of appeared trend's control panel to make the necessary navigation actions. To return the control panel of the parameter the left mouse button to click in an empty area of the frame is required.
Fig. 20 shows an example of this element in the runtime mode.
Fig.20. "Regulator's control panel" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
SHIFR	Code	String	Input link	Parameter|SHIFR
NAME	Name	String	Input link	Parameter|NAME
DESCR	Description	String	Input link	Parameter|DESCR
max	Scale maximum	Real	Input link	Parameter|max
min	Scale minimum	Real	Input link	Parameter|min
ed	Units	String	Input link	Parameter|ed
prec	Precision	Integer	Input link	Parametr|prec	Number of decimal places in value and set point of the PID.
var	Variable	String	Input link	Parameter|var
var_addr	Variable address	Address	Input link	Parameter|var	Address for the trend's building of the value.
PID - regulator
auto_addr	Mode	Address	Input link	Parameter|auto	Address for the "Automate" mode trend's building.
sp	Set point	Real	Input link	Parameter|sp
sp_addr	Set point address	Address	Input link	Parameter|sp	Address for the trend's building of the set point.
out	Out	Real	Input link	Parameter|out
out_addr	Out address	Address	Input link	Parameter|out	Address for the trend's building of the analog output.
Hdwn	Bottom output border	Real	Full link	Parameter|Hdwn	Restricting the values of the analog output on the bottom.
Hup	Top output border	Real	Full link	Parameter|Hup	Restricting the values of the analog output on the top.
Kp	Gain coefficient	Real	Full link	Parameter|Kp
Ki	Coeff. of integration	Real	Full link	Parameter|Ki
Ti	Integration time	Real	Full link	Parameter|Ti
Kd	Coeff. of differential	Real	Full link	Parameter|Kd
Td	Differentiation time	Real	Full link	Parameter|Td
Tzd	Differential part lag time	Real	Full link	Parameter|Tzd
Zi	Insensitivity area	Real	Full link	Parameter|Zi
K1	Input 1 coefficient	Real	Full link	Parameter|K1
K2	Input 2 coefficient	Real	Full link	Parameter|K2
K3	Input 3 coefficient	Real	Full link	Parameter|K3
K4	Input 4 coefficient	Real	Full link	Parameter|K4
Pulse PID - regulator
impQup_addr	Address of impulse output up	Address	Input link	Parameter|impQup	Address for the trend's building of the pulse output "Up".
impQdwn_addr	Address of impulse output down	Address	Input link	Parameter|impQdwn	Address for the trend's building of the pulse output "Down".
KImpRfact	Rate factor	Real	Full link	Parameter|KImpRfact	The asymmetry in the generation of pulse-width up and down.
TImpMin	Minimal impulse time	Integer	Full link	Parameter|TImpMin	There will be generated impulses, starting with the specified width.
TImpPer	Impulses period	Integer	Full link	Parameter|TImpPer	Frequency of repetition of pulse generation.

## 12. Root page (SO) (RootPgSo)
The "Root page" element, shown in Fig. 21, serves as the basis for creating the process control user interfaces, based on the signal object. The root page contains four areas:
- "Buttons-indicators area of the signal objects" (above) - is to provide information on the availability of alarms in the signal object and also to switch between them.
- "Buttons-modes of presentation area" (right-top) - indication of the selection and selection the presentation modes, such as: "Mnemo", "Graphics group", "Contours group", "Documents", etc. It also contains the quittance buttons that appear in the event of alarms and the page turning button of the mnemonic schemes.
- "Container of the mnemonic schemes and the basic frames of the operator interface" (center) - region of the container to place mnemonic schemes and basic frames at their selection by presentation modes buttons or at the change of the signal object.
- "Control panels container" (right-bottom) - region of the container to place control panels of various objects in the container of mnemonic schemes, for example: panel of the parameter, document, graphic (trend), etc.
Fig.21. "Root page (SO)" widget in the development mode.
### Using - Development
This widget can be used only in the root page mode that should be placed in the project's tree as an element "/*/so". In addition, around the main page should be made following tree hierarchy:
- "/*/control" - logical container containing a variety of control panels;
- "/*/so/{n}" - logical container of the signal object {n} (1 ... 16) contains the containers and the templates of presentation modes;
- "/*/so/{n}/mn" - logical container of the mnemonic schemes of the signal object contains many pages of final mnemonic schemes;
- "/*/so/{n}/ggraph" - graphics group template contains many pages of final graphics groups;
- "/*/so/{n}/gcadr" - contours group template contains many pages of final contours groups;
- "/*/so/{n}/gview" - overview frames panel template contours group overview frames groups;
- "/*/so/{n}/doc" - document's logical container contains many pages of the final documents;
- "/*/so/{n}/greg" - PID regulator's control panel page's template contains many pages of final PID regulators, statically linked;
- "/*/so/rg" - logical container result graphics - summary graphics for the operator interface;
- "/*/so/rg/rg" - result graphics template contains many pages of final result graphics.
### Using - Runtime
In the runtime mode, the user can select the desired from available signal object, select the type of presentation, make the quittance of alarms, and also cause the control panel for the the desired element. After choosing, the user is presented the mnemonic scheme or common frame in the mnemonic schemes container and control panel in the control panels container. Then the user can observe the state on mnemonic schemes and panels, as well as to the make actions provided by them.
Fig. 22 shows an example of this element in the runtime mode.
Fig.22. "Root page (SO)" widget in the runtime mode.
## 13. Passport (cntrPasp)
Element, shown in Fig. 23, is provided for displaying the parameter's passport: detailed information, including code, description, units, alarm borders, etc. Document is generated entirely dynamically.
### Using - Development
This element should be placed in a logical container of the project's tree. In development mode, the widget is a blank "Document", and therefore the only screen shot with this widget in the runtime mode of the project is provided. Linking with the parameter is made dynamically when you call "Passport" for the visual elements of the parameter.
### Using - Runtime
Calling the passport is made from the visual elements of parameter, for example: by right click of the mouse on the element "analog parameter" (anShow) and on the field of the "element cadr" widget (ElCadr) . After a call the separate window of the widget-passport with a list of all properties and values of the parameter as a table is opened.
 Fig.23. "Passport" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
pName	Parameter's name	Address	Input link	Parametr|NAME	Address to the parameter's name to refer to the parameter entirely and get all of its properties

## 14. Document panel (doc_panel)
Element, shown in Fig. 24, is used to manage documents and navigate through their histories. The element supports dynamic and archival documents.

Fig.24. "Document panel" widget in the development mode.
### Using - Development
This element should be placed in a logical panels' container of the project's tree. Linking with the parameter is dynamic when called from the document's element.
### Using - Runtime
Call of the panel is made from elements of the document. The panel provides tools that are somewhat different for dynamic and archival documents.
For dynamic document the following tools are provided:
- selection the time of the document's formation;
- selection the size of the document's formation;
- navigation through the document for one or five sizes of it;
- adjustment the time of generation of the document at the current time.
Archival document provides only navigation through documents in the archive by reversing them.
Fig. 25 shows examples of this element in the runtime mode: dynamic (left) and archival (right).

Fig.25. "Document panel" widget in the runtime mode.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
Dinamic document
time	Document time	DateTime	Full link	<page>|time
bTime	Document begin	DateTime	Full link	<page>|bTime
doc	Document	String	Full link	<page>|doc
Archive document
n	Archive size	Integer	Full link	<page>|n
vCur	View cursor	Integer	Full link	<page>|vCur

## 15. Graphics group panel (grph_panel)
Element, shown in Fig. 26, serves to control the "Diagram" widget, it allows you to view trends' history for the required period of time and the desired resolution, the scale, the selection of archiver for display and trends' presentation in a range of present frequencies are supported.

Fig.26. "Graphics group panel" widget in the development and runtime modes (left to right).
### Using - Development
This element should be placed in the logical container of the project's tree. Linking with the parameter is dynamic when called from a diagram element.
### Using - Runtime
Calling the panel is made from the diagram elements. The panel provides the following tools:
- time selection of the diagram formation;
- navigation through the diagram for the one or five sizes;
- adjustment of the diagram generation time to the current time;
- information about the time or frequency in the current cursor's position;
- selection of the diagram trends' presentation as the spectrum of frequencies;
- selection of the trend's formation size;
- selection of the archive, used for the trends' presentation;
- control the vertical scale of the presentation: zoom in and out the scale, shift the scale up and down, the scale returns to its original value.
### Linking attributes
ID	Parameter	Data type	Config	Config template	Description
tSek	Trend time	DateTime	Full link	<page>|tSek
tSize	Trend size	Real	Full link	<page>|tSize	Temporal size of the trend in the history from the time of the trend.
trcPer	Trace period	Integer	Full link	<page>|trcPer	Renewal period of the trend.
type	Type	String	Full link	<page>|type	Trend's type: regular or the frequency spectrum.
valArch	Archiver	String	Full link	<page>|valArch
curSek	Cursor	DateTime	Full link	<page>|curSek	Time of the cursor.
curUSek	Cursor, usec	Integer	Full link	<page>|curUSek	Time of cursor, microseconds.
sclVer	Vertical scale	Real	Full link	<page>|sclVerScl	The percentage of vertical scale.
sclVerOff	Vertical scale offset	Real	Full link	<page>|sclVerSclOff	Percentage of the offset on the vertical scale.

## 16. Terminator panel (terminator)
Element, shown in Fig. 27, serves to fill the empty place when no item is selected for control.

Fig.27. "Terminator panel" widget.
### Using - Development
This element should be placed in the logical container of the project's tree.
### Using - Runtime
Calling the panel is made from root page "RootPgSo" by changing the signal object or presentation mode.